## Cover Sheet
OM34440 Optus Site Feasibility Report |  |  |  | V | 5 | Cover Sheet
Site No. |  | H8097 | Site Name |  | Austins Ferry
NOTE: It is mandatory to complete the Cover Sheet and Site Access sheet for all projects
| Project |  | OHOB eJV 5G upgrade
| Description of proposed works |  | OHOB eJV 5G upgrade
NOTE: Always click the Unhide Worksheets button prior to pressing any alternative button
| JV Site ID |  | JH3038
| Optus Site Number |  | H8097 |  |  |  | Lead Operator |  | Optus
| Optus Site Name |  | Austins Ferry |  |  |  | Voda Site Name |  | Austins Ferry - V
| Optus Site Code |  | 77FE |  |  |  | Voda Site ID |  | 3819
Document Approval
|  |  | Signature |  |  |  |  | Name |  | Date
Lead PM
Lead RF
Non Lead RF
Lead Network Engineer
Has the Site Feasibility been fully approved ?
Completed Tabs
NOTE: Automatically populates dependant on your first question answer on each tab
| Feasibility Site Acquisition |  |  |  | Complete |  | Install & Commission Feasibility |  |  | Complete
| Cover Sheet |  |  |  | Yes |  | BTS |  |  | Yes
| Site Access |  |  |  | Yes |  | DC |  |  | Yes
| Property |  |  |  | Yes |  | TX |  |  | N/A
| Planning |  |  |  | Yes |  | Floor Layout |  |  | Yes
| Design |  |  |  | Yes |  | Antenna System |  |  | #REF!
[7 empty] | Photos |  |  | Yes
| Page Completed |  | Yes |  |  |  | By Whom |  | SARAVANAN S
| Company |  | ALL TELECOS |  |  |  | Date |  | 2025-09-13

## IC Works Summary
OM34440 Optus Site Feasibility Report |  |  | V | 5 | Feasibility Score of Works Summary
Site No. |  | H8097 | Site Name |  | Austins Ferry
NOTE: All Summaries are automatically imported from the Scope of Works Summary at the bottom of each tab
Construction Summary
1. ANTENNA SCOPE: SHARED : REPLACE EXISTING eJV 12P HUAWEI ASI4517R1 PANEL ANTENNAS (3 OFF) WITH NEW eJV 16P COMMSCOPE RRVV2VV-6533D-R8 PANEL ANTENNAS (1 OFF PER SECTOR) (FOR SECTOR 11-J, 21-J, & 31-J) ON NEW ANTENNA MOUNT CONNECTED TO NEW COLLAR MOUNT OPTUS : INSTALL NEW OPTUS ERICSSON AIR3268 B78Y (NR35) ANTENNAS (1 OFF PER SECTOR) (FOR SECTOR 12-O, 22-O, & 32-O) ON NEW ANTENNA MOUNT CONNECTED TO NEW COLLAR MOUNT VODAFONE : INSTALL NEW VODAFONE NOKIA AVQL (NR36) ANTENNAS (1 OFF PER SECTOR) (FOR SECTOR 13-V, 23-V, & 33-V) (BELOW OPTUS AAU) ON NEW ANTENNA MOUNT CONNECTED TO NEW COLLAR MOUNT 2. RRU SCOPE: OPTUS : REMOVE EXISTING OPTUS HUAWEI RRU3262 (L7) (3 OFF), RRU3936 (U9) (3 OFF), RRU3971 (L18) (3 OFF), RRU3971 (L21) (3 OFF) & RRU3281 (L26) (3 OFF). INSTALL NEW OPTUS ERICSSON RRU4480 (L7/NL9) (1 OFF PER SECTOR, 3 OFF TOTAL), RRU4466 (L18/NL21/L26) (1 OFF PER SECTOR, 3 OFF TOTAL) AND FUTURE RRU (2 OFF PER SECTOR, 6 OFF TOTAL) ON NEW RRU MOUNT CONNECTED TO NEW COLLAR MOUNT VODAFONE: REMOVE EXISTING VODAFONE HUAWEI RRU3952 (L850) (3 OFF), RRU3953 (U9) (3 OFF), RRU3971 (L18) (3 OFF) & RRU3971 (L21) (3 OFF). INSTALL NEW VODAFONE NOKIA RRU AHPB (N7) (1 OFF PER SECTOR, 3 OFF TOTAL), AHCA (L850) (1 OFF PER SECTOR, 3 OFF TOTAL) AND AHEGG (18/21) (2 OFF PER SECTOR, 6 OFF TOTAL) ON NEW RRU MOUNT CONNECTED TO NEW COLLAR MOUNT 3. COMBINER & MHA SCOPE: OPTUS : REMOVE EXISTING OPTUS COMBINERS COM2a (E12F13P25) (3 OFF) & COM3 (E16V90P56) (6 OFF). INSTALL NEW OPTUS REJ FILTER (E14V00P21) (1 OFF PER SECTOR, 3 OFF TOTAL) BEHIND NEW PANEL ANTENNAS ON NEW MOUNT VODAFONE: REMOVE EXISTING VODAFONE COMBINERS COM2 (E12F03P18) (3 OFF) & COM4 (E14F05P17) (6 OFF). INSTALL NEW VODAFONE COMBINER COM2g (E14F06P81) (1 OFF PER SECTOR, 3 OFF TOTAL) BEHIND NEW PANEL ANTENNAS ON NEW MOUNT 4. HYRBID SCOPE : OPTUS: REUSE EXISTING OPTUS H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND SHARED H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) TO BE ALLOCATED TO OPTUS TO RUN IN EXISTING OPTUS 450mm WIDE CABLE LADDER VODAFONE: REUSE EXISTING VODAFONE H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND INSTALL NEW H&S 9/18 (10mm2) HYBRID CABLES (1 OFF) (LENGTH: 40m) FOR VODAFONE TO RUN IN EXISTING OPTUS 450mm WIDE CABLE LADDER 5. GPS: OPTUS : REPLACE EXISTING OPTUS GPS ANTENNA (1 OFF) WITH NEW OPTUS ERICSSON GNSS GPS ANTENNA (1 OFF) ON THE TOP OF SHELTER WALL VODAFONE: INSTALL NEW VODAFONE NOKIA AYGE GPS ANTENNA (1 OFF) ON THE TOP OF SHELTER WALL. ENSURE MIN. 500mm HORIZONTAL SEPERATION FROM OTHER GPS ANTENNA
BTS Summary
OPTUS NOTES: 1. REMOVE EXISTING OPTUS HUAWEI BBU AND DCDU FROM THE RACK AT G001F04. 2. INSTALL NEW 1 x ERICSSON BBU6672 FOR L7/NL9/L18/NL21/L26/NR35 IN RACK AT G001F04. 3. INSTALL NEW DCDU (1 OFF) TO POWER UP ERICSSON BBUs IN RACK AT G001F04. 4. ALL EXTERNAL ALARMS (ENVIRONMENTAL ETC) TO BE MIGRATED FROM UMTS BBU TO LTE/5G BBU, AS PER OPTUS STANDARDS, INCLUDING OM36991 RAN EQUIPMENT I&C STANDARDS. 5. ALL 3G CONTROLLED RET'S TO BE MIGRATED TO 4G/5G AS REQUIRED, ACCORDING TO OPTUS STANDARDS, INCLUDING OM38040 MIMO PORT PLUMBING BTS RET CONTROL DEPLOYMENT. 6. REMOVE ANY ON-SITE CCU'S AND CONVERT CCU CONTROLLED MHA'S TO BTS CONTROLLED 7. EXISTING KRONE PANEL TO BE UPGRADED TO RJ45 PATCH PANEL. INSTALL 1 x 6610 FOR PSU ALARM AT G000.F02. iDCDP NOTES: 8. REUSE EXISTING OPTUS 22-WAY LENMIC iDCDP (1 OFF) IN RACK AT G001F05. AND SWAP CBs ON PSU AND iDCDP AS PER LATEST GUIDELINE. VODAFONE NOTES: 9. REMOVE EXISTING VODAFONE HUAWEI BBU AND DCDU FROM THE RACK AT G001F02. 10. INSTALL NEW NOKIA AIRSCALE/AMID CHASIS 1 OFF WITH SUITABLE BB CARDS AS PER EBP IN RACK AT G001F02. 11. NOKIA AIRSCALE SHALL BE POWER UP VIA VODAFONE PSU IN RACK AT G000F04. 12. NOKIA TX ROUTER TO BE RELOACTED FROM RU7 TO RU18 OR HIGHER POSTION AT G000F02. iDCDP NOTES: 13. REUSE EXISTING VODAFONE 22-WAY LENMIC iDCDP (1 OFF) IN RACK AT G001F05. AND SWAP CBs ON PSU AND iDCDP AS PER LATEST GUIDELINE.
DC Summary
OPTUS DC POWER UPGRADE: 1. REMOVE EXISTING OPTUS HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F03. 2. INSTALL NEW OPTUS 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F03. 3. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F03. 4. REPLACE EXISTING 32A 1P CB (3 OFF) WITH NEW 40A 1P CB (3 OFF) FOR OPTUS PSU ON THE DISTRIBUTION BOARD. 5. OPTUS POWER TOOL V12.7 APPROVED. 6. DIVERSIFY Tx FEEDS OVER 2 PSUs. APDP FEED A ON OPTUS PSU-1-O. FEED B ON VODAFONE PSU-2-V. VODAFONE DC POWER UPGRADE: 7. REMOVE EXISTING VODAFONE HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F04. 8. INSTALL NEW VODAFONE 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F04. 9. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F04. 10. REPLACE EXISTING 32A 1P CB (3 OFF) WITH NEW 40A 1P CB (3 OFF) FOR VODAFONE PSU ON THE DISTRIBUTION BOARD.
TX Summary
0
Floor Layout Summary
OPTUS NOTES: 1. REMOVE EXISTING OPTUS HUAWEI BBU AND DCDU FROM THE RACK AT G001F04. 2. INSTALL NEW 1 x ERICSSON BBU6672 FOR L7/NL9/L18/NL21/L26/NR35 IN RACK AT G001F04. 3. INSTALL NEW DCDU (1 OFF) TO POWER UP ERICSSON BBUs IN RACK AT G001F04. 4. ALL EXTERNAL ALARMS (ENVIRONMENTAL ETC) TO BE MIGRATED FROM UMTS BBU TO LTE/5G BBU, AS PER OPTUS STANDARDS, INCLUDING OM36991 RAN EQUIPMENT I&C STANDARDS. 5. ALL 3G CONTROLLED RET'S TO BE MIGRATED TO 4G/5G AS REQUIRED, ACCORDING TO OPTUS STANDARDS, INCLUDING OM38040 MIMO PORT PLUMBING BTS RET CONTROL DEPLOYMENT. 6. REMOVE ANY ON-SITE CCU'S AND CONVERT CCU CONTROLLED MHA'S TO BTS CONTROLLED 7. EXISTING KRONE PANEL TO BE UPGRADED TO RJ45 PATCH PANEL. INSTALL 1 x 6610 FOR PSU ALARM AT G000.F02. iDCDP NOTES: 8. REUSE EXISTING OPTUS 22-WAY LENMIC iDCDP (1 OFF) IN RACK AT G001F05. AND SWAP CBs ON PSU AND iDCDP AS PER LATEST GUIDELINE. HYBRID CABLE NOTES: 9. REUSE EXISTING OPTUS H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND SHARED H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) DC POWER UPGRADE: 10. REMOVE EXISTING OPTUS HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F03. 11. INSTALL NEW OPTUS 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F03. 12. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F03. 13. REPLACE EXISTING 32A 1P CB (3 OFF) WITH NEW 40A 1P CB (3 OFF) FOR OPTUS PSU ON THE DISTRIBUTION BOARD. 14. OPTUS POWER TOOL V12.7 APPROVED. 15. DIVERSIFY Tx FEEDS OVER 2 PSUs. APDP FEED A ON OPTUS PSU-1-O. FEED B ON VODAFONE PSU-2-V. AC POWER UPGRADE: 16. EXISTING OPTUS 50A THREE PHASE POWER SUPPLY IS SUFFICIENT FOR THE PROPOSED UPGRADE. VODAFONE NOTES: 17. REMOVE EXISTING VODAFONE HUAWEI BBU AND DCDU FROM THE RACK AT G001F02. 18. INSTALL NEW NOKIA AIRSCALE/AMID CHASIS 1 OFF WITH SUITABLE BB CARDS AS PER EBP IN RACK AT G001F02. 19. NOKIA AIRSCALE SHALL BE POWER UP VIA VODAFONE PSU IN RACK AT G000F04. 20. NOKIA TX ROUTER TO BE RELOACTED FROM RU7 TO RU18 OR HIGHER POSTION AT G000F02. iDCDP NOTES: 21. REUSE EXISTING VODAFONE 22-WAY LENMIC iDCDP (1 OFF) IN RACK AT G001F05. AND SWAP CBs ON PSU AND iDCDP AS PER LATEST GUIDELINE. HYBRID CABLE NOTES: 22. REUSE EXISTING VODAFONE H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND INSTALL NEW H&S 9/18 (10mm2) HYBRID CABLES (1 OFF) (LENGTH: 40m) DC POWER UPGRADE: 23. REMOVE EXISTING VODAFONE HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F04. 24. INSTALL NEW VODAFONE 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F04. 25. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F04. 26. REPLACE EXISTING 32A 1P CB (3 OFF) WITH NEW 40A 1P CB (3 OFF) FOR VODAFONE PSU ON THE DISTRIBUTION BOARD.
Antenna System Summary
#REF!

## Site Access
OM34440 Optus Site Feasibility Report | [5 empty] | V | 5 | Site Access Details
Site No. |  | H8097 |  | Site Name |  |  | Austins Ferry
NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study.
| Are you required to perform a feasibility study on the site? | [11 empty] | Yes
Details
| JV Site Number |  |  | JH3038
| Optus Site Name |  |  | Austins Ferry
Pink Cells will automatically be updated from information entered on the Cover Sheet
| Optus Site Number |  |  | H8097
| Optus Site Code |  |  | 77FE
| Voda Site Name |  |  | Austins Ferry - V
| Voda Site ID |  |  | 3819
| Site Address |  |  | 2 Plan 158154 Wakehurst Rd, AUSTINS FERRY TAS 7011
| Postcode |  |  | 7011
| Longitude JDA94 |  |  | 147.2451 |  |  |  |  | Latitude JDA94 | Latitude |  | -42.7782
Special Access Instructions
ENTER POIMENA RESERVE FROM WAKEHURST ROAD AND TRAVEL TO UPPER CARPARK. OPTUS TO DAISY CHAIN LOCK INTO GATE TO GAIN ACCESS TO GATE.
TRAVEL UP EXISTING ACCESS TRACK TO TELSTRA FACILITY.
(NOTE: ACCESS TRACK IS ON/NEXT TO FRISBEE GOLF COURSE, CAUTION SHOULD BE TAKEN)
| Site Owner | [9 empty] | Other
| Details |  | Glenorchy City Council
| Structure Type | [9 empty] | Monopole
| Details |  | 27m HIGH CONCRETE MONOPOLE (SR3-BM27-585).
| Structure Owner | [9 empty] | Optus
| Details |  | Optus
| Equipment Enclosure Type | [9 empty] | Sandwich Panel Shelter
| Details |  | OPTUS ZONECOOL C3 (3.0m x 2.5m) EQUIPMENT SHELTER.
| Greenfield Site | [9 empty] | No
Details
Site Access
(Add specific key, Property Manager, 24/7 access to the Details section when required)
| Is a special permit required for access? | [8 empty] | (If yes complete the details below) | No
Details
| Are access times restricted? | [9 empty] | No
Details
| Is a Security Escort required? | [9 empty] | No
Details
| Is a Special key required? | [9 empty] | Yes
| Details |  | OPTUS TO DAISY CHAIN LOCK INTO GATE TO GAIN ACCESS TO GATE.
| Is an induction required | [9 empty] | No
Details
| Has the Lad Safe been certified? | [9 empty] | N/A
| Details |  | LAD-SAF not available
Equipment Delivery
| Is a 4WD or special vehicle required? | [9 empty] | Yes
| Details |  | SITE IS ACCESSED THROUGH DIRT ACCESS TRACK (UPHILL)
| Is there parking available on site? | [9 empty] | Yes
Details
| Are there any restrictions on shelter deliveries being made? | [9 empty] | No
Details
| Is an EWP (crane or cherry picker required?) | [9 empty] | Yes
| Details |  | Antenna acess only via EWP
| Do you have to use stairs to access the shelter? (how many?) | [9 empty] | No
Details
| Is a special delivery tool required?(wheel trolley, lifting bag?) | [9 empty] | No
Details
| Are there any special instructions for equipment delivery? | [9 empty] | No
Details
| Is there space in the shelter/ site to unpack/store deliveries? | [9 empty] | Yes
Details
| Can an unmanned delivery be made? | [9 empty] | No
Details
| Are there any other delivery details that need to be outlined? | [9 empty] | No
Details
| Page Completed |  |  |  | Yes |  |  |  | By Whom |  |  | SARAVANAN S
| Company |  |  |  | ALL TELECOS |  |  |  | Date |  |  | 2025-09-13
Note on P36: Who is the leading carrier that owns the facility
Note on P60: Do you have to contact anyone prior to accessing the site, example West Gate Bridge Melbourne, City link need to be contacted to access the site.
Note on P65: Can you access the site 24/7 without any special conditions required, if so it is not restricted.
Note on P77: E.g. Major shopping centres and corporations may require an induction to allow you to safely enter there premises
Note on P81: The Ladsafe or ladder fall arrest system must have a stamp indicating an inspections has been carried out within the last year.
Note on E97: copy & paste details from MSL

## Property
OM34440 Optus Site Feasibility Report |  |  |  | V | 5 | Property
Site No. |  | H8097 |  | Site Name |  | Austins Ferry
NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study.
| Are you required to perform a feasibility study on the site? | [6 empty] | Yes
Details
| Do both operators have separate ground/rooftop leases ? | [6 empty] | Yes
| Details | Lease with Glenorchy City Council
| Landlord - Ground Lease? | [6 empty] | Local Council
| Details | Lease with Glenorchy City Council
| Landlord - Structure Lease? | [6 empty] | Optus
| Details | Optus owned tower
| Is this a Greenfield Site ? | [6 empty] | No
| Details | Upgrade 5G (EJV OH)
Property Tenure Considerations
| Lease or Licence |  |  | 1. Tower licence with Amplitel 2. Ground Lease with Glenorchy City Council
| Lessor or Licensor |  |  | Lessor
| Co-locate / Co-Site (e.g. Crown Castle, Telstra, etc) |  |  | co-site to Telstra
| Type & Structure (e.g. tower, rooftop, reservoir, etc) |  |  | Monopole
| Tenure | Period |  | 01.01.2022 to 31.05.2036 (14 years 5 months)
|  | Commencement |  | 01.01.2022
|  | Remaining |  | 10 years and 8 months
|  | Current Rental & Escalation |  | 1.Tower licence fee - as per Optus/Amplitel MAA 2. Ground lease - $16,390.91 + 3% Esc.
|  | Special Conditions |  | Yes -Market rent review every 5 years
|  | Sub-Lease |  | Optus may sublet the premises upon written notice to the Lessor- Refer to clause 12.4
|  | Renegotiation Required |  | N
| Rental Increase expected? Y/N |  |  | N
If yes, please provide estimated increase
| Lease / licence area variation requirements |  |  | n/a
| Limitations on expansion of lease area |  |  | No
| Consent requirements for additional equipment |  |  | CNTBUW - Refer to clause 8.2
| Consent required for sub-lease / licence |  |  | Optus may sublet the premises upon written notice to the Lessor- Refer to clause 12.4
| Other conditions pertaining to site (e.g. access, security) |  |  | AOR - Refer to Clause 5.2 & Clause 6
| Other Carrier Implications |  |  | Co-site notice to Telstra
| Does Lease/Licence contain a redevelopment clause? - Y/N |  |  | N
| If Yes, will redevelopment be invoked in the near future? |  |  | n/a
| B-end acquisition works required? - Y/N If Yes, perform property tenure considerations for B-end) |  |  | N
Property Risk Assessment
| Details | Optus owned structure. Works require council's consent - CNTBUW. Site access is through another lot also owned by council. Co-site notice will be required for Telstra in Phase 2.
| Page Completed |  | Yes |  |  | By Whom | Akhil Davuluri
| Company |  | CPS Tech |  |  | Date | 16.09.25

## Planning
OM34440 Optus Site Feasibility Report |  |  |  | V | 5 | Planning
Site No. |  | H8097 |  | Site Name |  | Austins Ferry
NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study.
| Are you required to perform a feasibility study on the site? | [6 empty] | Yes
Details
Environmental Planning Considerations
| 25% volume increase compromised ? |  |  | TBC
| Adjoining Council notification |  |  | No
| Area (Part 2 of LIFD) |  |  | Residential
| Area of Environmental Significance (ES) |  |  | No
| Associated Timeframe |  |  | 2-4 weeks
| CA Deployment Category |  |  | DC7
| Community Sensitivity (TLM) |  |  | Amber
| Community Sensitivity Comments |  |  | Previous deployments received no comments or submissions. While properties to the north may have clearer views due to reduced vegetation, the upgrade will have minimal visual impact as it does not increase the structure’s height or volume.
| General Site Area Comments |  |  | The site is located within an open space/reserve area surrounded by residential suburbs. Due to its elevated position and surrounding vegetation, visual impacts are minimal. The land is subject to a bushfire overlay, which should be considered during further due diligence; however, this is unlikely to affect the upgrade as both the monopole and equipment shelter are existing structures
| Heritage / Environmental Comments |  |  | No
| Local Government Area (LGA) e.g. shire, council etc |  |  | Glenorchy City Counil
| Low Impact site |  |  | Yes
| Maintenance? |  |  | No
| Non-Low Impact? Provide reason? |  |  | NA
| Other area of Environment Significance (For ACMA & ACIF Compliance - take photos and note distances etc) |  |  | No
| Other relevant Statutory Authorities (e.g. PALM, DUAP) |  |  | NA
| Principle Designated Use |  |  | Open/Public space
| Relevant documents (e.g. LEP, DCP) |  |  | Telecommunications (Low-Impact Facilities) Determination 2018, Deployment Code
| Zone |  |  | Open Space
Environmental Risk Assessment
Details
The land is within an open space zone, and is subject to a Bushfire-prone overlay and priority vegetation overlay. Given that the scope of works is for an upgrade of existing panel antennas as well as ancillary equipment, and the fact there will be no increase in height to the lattice tower, nor any new or replacement of equipment shelters, these overlays should not impact the low impact status of the proposal.
Recommended Strategy
Details
Deployment Code 7 notification, Letters to Glenorchy Council, State & Fed MP, IAP letters and a Sign on site, estimated time 12 business days
| Page Completed |  | Yes |  |  | By Whom | Tiana Sinopoli
| Company |  | CPS Technology & Infrastrucutre |  |  | Date | 2025-09-16

## Design
OM34440 Optus Site Feasibility Report |  |  |  | V | 5 | Design
Site No. |  | H8097 |  | Site Name |  | Austins Ferry
NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study.
| Are you required to perform a feasibility study on the site? | [7 empty] | Yes
Details
Structure Type
| Structure Type |  | Monopole
| Structure Owner |  | Optus
| Manufacturer & Model |  | ROCLA CONCRETE MONOPOLE & SR3-BM27-585
| Structure Height |  | 27m
| Antenna Height |  | 23.10m & 24.10m
| Structure Loading |  | 99%
| Foundation Loading |  | 99%
| Details | Refer to Pole certificate 292920_1 by Civilmart
Condition of Existing Mounts & Sundry Supports
| Sector | Mount | Type | Length | Describe Works Required to Upgrade for Target Antenna Solution
| 1 | New Antenna mount | CHS | 2.7m | SHARED : REPLACE EXISTING eJV 12P HUAWEI ASI4517R1 PANEL ANTENNAS (3 OFF) WITH NEW eJV 16P COMMSCOPE RRVV2VV-6533D-R8 PANEL ANTENNAS (1 OFF PER SECTOR) (FOR SECTOR 11-J, 21-J, & 31-J) ON NEW ANTENNA MOUNT CONNECTED TO NEW COLLAR MOUNT OPTUS : INSTALL NEW OPTUS ERICSSON AIR3268 B78Y (NR35) ANTENNAS (1 OFF PER SECTOR) (FOR SECTOR 12-O, 22-O, & 32-O) ON NEW ANTENNA MOUNT CONNECTED TO NEW COLLAR MOUNT VODAFONE : INSTALL NEW VODAFONE NOKIA AVQL (NR36) ANTENNAS (1 OFF PER SECTOR) (FOR SECTOR 13-V, 23-V, & 33-V) (BELOW OPTUS AAU) ON NEW ANTENNA MOUNT CONNECTED TO NEW COLLAR MOUNT
| 2 | New Antenna mount | CHS | 2.7m
| 3 | New Antenna mount | CHS | 2.7m
Details
Cable Ladder
Describe existing cable ladder, size mounting method, etc
| Sector 1 | ALL CABLES TO BE RUN IN EXISTING 450 WIDE ELEVATED CABLE LADDER
Sector 2
Sector 3
Sector 4
Describe works required to upgrade for Target Antenna Solution
| Sector 1 | OPTUS: REUSE EXISTING OPTUS H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND SHARED H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) TO BE ALLOCATED TO OPTUS TO RUN IN EXISTING OPTUS 450mm WIDE CABLE LADDER VODAFONE: REUSE EXISTING VODAFONE H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND INSTALL NEW H&S 9/18 (10mm2) HYBRID CABLES (1 OFF) (LENGTH: 40m) FOR VODAFONE TO RUN IN EXISTING OPTUS 450mm WIDE CABLE LADDER
Sector 2
Sector 3
Sector 4
Details
Other Carriers On Site (Mark X in relevant boxes)
| Telstra | 3GIS | Voda |  | Others
| X |  | X
Details
Shelter Fit Out
| Shelter/Cabinet type & details |  |  | Sandwich Panel Shelter
| Is there any floor space available |  |  | YES
| Does the existing Gland Window have sufficient space for new feeders |  |  | YES
| Cable ladder capacity sufficient |  |  | YES
Details
| Shelter Air Conditioning and Economy Fan | [9 empty] | Eeprom List
[11 empty] | Site Type | Version | Temp On Set Point | Last Updated
| Air Conditioner 1 Make and Model | [9 empty] | Standard Site Use | A2E81_3(A/D) | 33.5 Degrees C | 2015-10-12
| Air Conditioner 2 Make and Model | [9 empty] | Hub Site with Alcatel 1662 use | A2E82_3(A/D) | 31 Degrees C | 2015-10-12
| Air Conditioner 3 Make and Model | [9 empty] | Leave Existing Eeprom
| Does shelter have an economy fan installed? |  |  | NO | [6 empty] | N/A
If no econ fan installed detail works required to install fan, PLC, motorised air relief & ancillaries.
eProm Version required (if installing/upgrading e fan)
Detail any other air conditioner works required.
Details
AC Power Supply
Phase Options
|  | Meter Box / Pillar |  | AC Distribution Board | [6 empty] | RED
|  | Main Breaker |  | Pwr System Breaker 1 | Pwr System Breaker 2 | Pwr System Breaker 3 | Air Con 1 Breaker | Air Con 2 Breaker | Air Con 3 Breaker | eFan Breaker | WHITE
| Existing Phase(s) | 3 |  | N/A | N/A | [5 empty] | BLUE
| Existing Size | 50A |  | 32A | 32A | [5 empty] | N/A
| Proposed Phase(s) | 3 |  | N/A | N/A | [5 empty] | SINGLE PHASE
| Proposed Size | 50A |  | 40A | 40A
Other
| Details | EXISTING OPTUS 50A THREE PHASE POWER SUPPLY IS SUFFICIENT FOR PROPOSED UPGRADE
-Also refer to Power Calculator tab
Additional Information
Comments on 3rd Party installs that compromise access or lease area or power requirements
Redline Mark Drawings
You need to paste these in
Include a redlined marked up copy of the most recent drawings outlining the proposal, example is provided below.
Fill in the Scope of Works Summary box below with as much details as possible relating to the proposed construction and shelter upgrade works.
1. ANTENNA SCOPE: SHARED : REPLACE EXISTING eJV 12P HUAWEI ASI4517R1 PANEL ANTENNAS (3 OFF) WITH NEW eJV 16P COMMSCOPE RRVV2VV-6533D-R8 PANEL ANTENNAS (1 OFF PER SECTOR) (FOR SECTOR 11-J, 21-J, & 31-J) ON NEW ANTENNA MOUNT CONNECTED TO NEW COLLAR MOUNT OPTUS : INSTALL NEW OPTUS ERICSSON AIR3268 B78Y (NR35) ANTENNAS (1 OFF PER SECTOR) (FOR SECTOR 12-O, 22-O, & 32-O) ON NEW ANTENNA MOUNT CONNECTED TO NEW COLLAR MOUNT VODAFONE : INSTALL NEW VODAFONE NOKIA AVQL (NR36) ANTENNAS (1 OFF PER SECTOR) (FOR SECTOR 13-V, 23-V, & 33-V) (BELOW OPTUS AAU) ON NEW ANTENNA MOUNT CONNECTED TO NEW COLLAR MOUNT 2. RRU SCOPE: OPTUS : REMOVE EXISTING OPTUS HUAWEI RRU3262 (L7) (3 OFF), RRU3936 (U9) (3 OFF), RRU3971 (L18) (3 OFF), RRU3971 (L21) (3 OFF) & RRU3281 (L26) (3 OFF). INSTALL NEW OPTUS ERICSSON RRU4480 (L7/NL9) (1 OFF PER SECTOR, 3 OFF TOTAL), RRU4466 (L18/NL21/L26) (1 OFF PER SECTOR, 3 OFF TOTAL) AND FUTURE RRU (2 OFF PER SECTOR, 6 OFF TOTAL) ON NEW RRU MOUNT CONNECTED TO NEW COLLAR MOUNT VODAFONE: REMOVE EXISTING VODAFONE HUAWEI RRU3952 (L850) (3 OFF), RRU3953 (U9) (3 OFF), RRU3971 (L18) (3 OFF) & RRU3971 (L21) (3 OFF). INSTALL NEW VODAFONE NOKIA RRU AHPB (N7) (1 OFF PER SECTOR, 3 OFF TOTAL), AHCA (L850) (1 OFF PER SECTOR, 3 OFF TOTAL) AND AHEGG (18/21) (2 OFF PER SECTOR, 6 OFF TOTAL) ON NEW RRU MOUNT CONNECTED TO NEW COLLAR MOUNT 3. COMBINER & MHA SCOPE: OPTUS : REMOVE EXISTING OPTUS COMBINERS COM2a (E12F13P25) (3 OFF) & COM3 (E16V90P56) (6 OFF). INSTALL NEW OPTUS REJ FILTER (E14V00P21) (1 OFF PER SECTOR, 3 OFF TOTAL) BEHIND NEW PANEL ANTENNAS ON NEW MOUNT VODAFONE: REMOVE EXISTING VODAFONE COMBINERS COM2 (E12F03P18) (3 OFF) & COM4 (E14F05P17) (6 OFF). INSTALL NEW VODAFONE COMBINER COM2g (E14F06P81) (1 OFF PER SECTOR, 3 OFF TOTAL) BEHIND NEW PANEL ANTENNAS ON NEW MOUNT 4. HYRBID SCOPE : OPTUS: REUSE EXISTING OPTUS H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND SHARED H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) TO BE ALLOCATED TO OPTUS TO RUN IN EXISTING OPTUS 450mm WIDE CABLE LADDER VODAFONE: REUSE EXISTING VODAFONE H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND INSTALL NEW H&S 9/18 (10mm2) HYBRID CABLES (1 OFF) (LENGTH: 40m) FOR VODAFONE TO RUN IN EXISTING OPTUS 450mm WIDE CABLE LADDER 5. GPS: OPTUS : REPLACE EXISTING OPTUS GPS ANTENNA (1 OFF) WITH NEW OPTUS ERICSSON GNSS GPS ANTENNA (1 OFF) ON THE TOP OF SHELTER WALL VODAFONE: INSTALL NEW VODAFONE NOKIA AYGE GPS ANTENNA (1 OFF) ON THE TOP OF SHELTER WALL. ENSURE MIN. 500mm HORIZONTAL SEPERATION FROM OTHER GPS ANTENNA
Information will be automatically generated to the IC Works Summary tab
| Page Completed |  | Yes |  |  | By Whom | SARAVANAN S
| Company |  | ALL TELECOS |  |  | Date | 2025-09-13
Note on E13: Pink Cells are automatically updated from the Site Access tab
Note on E14: Pink Cells are automatically updated from the Site Access tab
Note on F62: Pink Cells are automatically updated from the Site Access tab

## BTS
OM34440 Optus Site Feasibility Report | [6 empty] | V | 5 | BTS Details
Site No. |  | H8097 |  |  | Site Name |  |  | Austins Ferry
NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study.
| Are you performing a feasibility on the BTS system? | [13 empty] | Yes
Details
Existing BTS Technologies
| Suite Number |  |  | Operator |  | Vendor |  | Cabinet |  | Band |  | Technology | TX Type |  | BTS Recovery Required | Combiner Used
| G001F04 |  |  | Optus |  | ICS |  | RACK |  | 7/18/21/26 |  | LTE | IP |  | Yes | Yes
| G001F04 |  |  | Optus |  | ICS |  | RACK |  | 9/21 |  | UMTS | IP |  | Yes | Yes
| G001F02 |  |  | Voda |  | ICS |  | RACK |  | 85/18/21 |  | LTE | IP |  | Yes | Yes
| G001F02 |  |  | Voda |  | ICS |  | RACK |  | 9 |  | UMTS | IP |  | Yes | Yes
Details
| Which BTS is monitoring Environmental alarms? | [13 empty] | Other
| Details |  | EXISTING Tx MER RACK
| Are two footprints available for each carrier? | [10 empty] | No |  |  | Yes
| Details |  | Spare Racks available
| Are you installing a BTS/s into an MER Rack? | [10 empty] | No |  |  | Yes
Details
Proposed BTS Technologies
| Suite Number |  |  | Operator |  | Vendor |  | Cabinet |  | Band |  | Technology | TX Type |  | Floor space Recovered | Combiner Used
| G001F04 |  |  | Optus |  | ICS |  | RACK |  | 7/18/26 |  | LTE | IP |  | N/A | No
| G001F04 |  |  | Optus |  | ICS |  | RACK |  | 9/21 |  | LTE / NR | IP |  | N/A | No
| G001F04 |  |  | Optus |  | ICS |  | RACK |  | 35 |  | NR | IP |  | N/A | No
| G001F02 |  |  | Voda |  | ICS |  | RACK |  | .85/18/21 |  | LTE | IP |  | N/A | Yes
| G001F02 |  |  | Voda |  | ICS |  | RACK |  | 7/36 |  | NR | IP |  | N/A | Yes
Details
| Which BTS will be monitoring Environmental alarms? | [13 empty] | Other
| Which BTS technology is proposed to provide RET control? | [13 empty] | Other
| Suite |  | G001F04
Fill in the Scope of Works Summary box below with as much details as possible relating to the proposed BTS upgrade site works.
OPTUS NOTES: 1. REMOVE EXISTING OPTUS HUAWEI BBU AND DCDU FROM THE RACK AT G001F04. 2. INSTALL NEW 1 x ERICSSON BBU6672 FOR L7/NL9/L18/NL21/L26/NR35 IN RACK AT G001F04. 3. INSTALL NEW DCDU (1 OFF) TO POWER UP ERICSSON BBUs IN RACK AT G001F04. 4. ALL EXTERNAL ALARMS (ENVIRONMENTAL ETC) TO BE MIGRATED FROM UMTS BBU TO LTE/5G BBU, AS PER OPTUS STANDARDS, INCLUDING OM36991 RAN EQUIPMENT I&C STANDARDS. 5. ALL 3G CONTROLLED RET'S TO BE MIGRATED TO 4G/5G AS REQUIRED, ACCORDING TO OPTUS STANDARDS, INCLUDING OM38040 MIMO PORT PLUMBING BTS RET CONTROL DEPLOYMENT. 6. REMOVE ANY ON-SITE CCU'S AND CONVERT CCU CONTROLLED MHA'S TO BTS CONTROLLED 7. EXISTING KRONE PANEL TO BE UPGRADED TO RJ45 PATCH PANEL. INSTALL 1 x 6610 FOR PSU ALARM AT G000.F02. iDCDP NOTES: 8. REUSE EXISTING OPTUS 22-WAY LENMIC iDCDP (1 OFF) IN RACK AT G001F05. AND SWAP CBs ON PSU AND iDCDP AS PER LATEST GUIDELINE. VODAFONE NOTES: 9. REMOVE EXISTING VODAFONE HUAWEI BBU AND DCDU FROM THE RACK AT G001F02. 10. INSTALL NEW NOKIA AIRSCALE/AMID CHASIS 1 OFF WITH SUITABLE BB CARDS AS PER EBP IN RACK AT G001F02. 11. NOKIA AIRSCALE SHALL BE POWER UP VIA VODAFONE PSU IN RACK AT G000F04. 12. NOKIA TX ROUTER TO BE RELOACTED FROM RU7 TO RU18 OR HIGHER POSTION AT G000F02. iDCDP NOTES: 13. REUSE EXISTING VODAFONE 22-WAY LENMIC iDCDP (1 OFF) IN RACK AT G001F05. AND SWAP CBs ON PSU AND iDCDP AS PER LATEST GUIDELINE.
Information will be automatically generated to the IC Works Summary tab
| Page Completed |  |  |  |  | Yes |  |  |  |  | By Whom |  |  | SARAVANAN S
| Company |  |  |  |  | ALL TELECOS |  |  |  |  | Date |  |  | 2025-09-13
Note on E56: Enter the suite number of the BTS monitoring the environmental and Power supply alarms
Note on C60: Insert information relevant to intended works on site and how you plan to complete.

## DC
OM34440 Optus Site Feasibility Report | [6 empty] | V | 5 | DC Supply Details | [8 empty] | OM34440 Optus Site Feasibility Report |  | V | 5 | Power Calculations Summary Report
Site No. |  | H8097 |  |  | Site Name |  |  | Austins Ferry | [9 empty] | Site No. | Austins Ferry | Site Name |  |  | H8097
| NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study. | [16 empty] | Power Calculations Summary Report can be generated with OM38347 Optus Power Calculator. Once the report is generated, copy the report as instructed in OM38347, Click the Red Box below and paste (ctrl-v) the report below.
| Are you performing a feasibility on the DC system? | [15 empty] | Yes
| Details | [16 empty] | PASTE
NOTE: Refer to the DC Power Calculator for equipment current draw and final DC supply requirements. EJV sites require two separate power supplies one for carrier.
Existing DC Solution
| Suite Number |  |  | Operator |  | Vendor |  |  |  | Battery String Quantity |  | Rectifier Quantity |  | Current Draw Amps |  | DC Recovery Required
| G000FO3 |  |  | Optus |  | HUAWEI |  |  |  | 5 |  | 6 |  | - |  | Yes
| G000FO4 |  |  | Voda |  | HUAWEI |  |  |  | 5 |  | 6 |  | - |  | Yes
Proposed DC Solution
| Suite Number |  |  | Operator |  | Vendor |  |  |  | Battery String Quantity |  | Rectifier Quantity |  | Current Draw Amps |  | DC Recovery Required
| G000FO3 |  |  | Optus |  | VERTIV |  |  |  | 5 |  | 6 |  | - |  | NA
| G000FO4 |  |  | Voda |  | VERTIV |  |  |  | 5 |  | 6 |  | - |  | NA
| Does an upgrade need to be performed? | [15 empty] | Yes
| Details |  | OPTUS DC POWER UPGRADE: 1. REMOVE EXISTING OPTUS HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F03. 2. INSTALL NEW OPTUS 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F03. 3. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F03. VODAFONE DC POWER UPGRADE: 4. REMOVE EXISTING VODAFONE HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F04. 5. INSTALL NEW VODAFONE 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F04. 6. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F04.
| Are any new circuit breakers required? | [9 empty] | No | [5 empty] | Yes
| Details |  | REFER iDCDP LAYOUT
Proposed Circuit Breaker layout Power Supply 1
Allocate equal number of positions for each operator + 4 positions for TXMN
| Position |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Size
Allocation
| Position |  |  |  |  | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Size
Allocation
Details
Proposed Circuit Breaker layout Power Supply 2
Allocate equal number of positions for each operator + 4 positions for TXMN
| Position |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Size
Allocation
| Position |  |  |  |  | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Size
Allocation
Details
| Are any new DC cable lengths required? |  |  |  |  | 18: Yes; 24: Yes
| Details |  | OPTUS: REUSE EXISTING OPTUS H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND SHARED H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) TO BE ALLOCATED TO OPTUS VODAFONE: REUSE EXISTING VODAFONE H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND INSTALL NEW H&S 9/18 (10mm2) HYBRID CABLES (1 OFF) (LENGTH: 40m) FOR VODAFONE
Fill in the Scope of Works Summary box below with as much details as possible relating to proposed power system upgrade site works.
OPTUS DC POWER UPGRADE: 1. REMOVE EXISTING OPTUS HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F03. 2. INSTALL NEW OPTUS 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F03. 3. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F03. 4. REPLACE EXISTING 32A 1P CB (3 OFF) WITH NEW 40A 1P CB (3 OFF) FOR OPTUS PSU ON THE DISTRIBUTION BOARD. 5. OPTUS POWER TOOL V12.7 APPROVED. 6. DIVERSIFY Tx FEEDS OVER 2 PSUs. APDP FEED A ON OPTUS PSU-1-O. FEED B ON VODAFONE PSU-2-V. VODAFONE DC POWER UPGRADE: 7. REMOVE EXISTING VODAFONE HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F04. 8. INSTALL NEW VODAFONE 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F04. 9. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F04. 10. REPLACE EXISTING 32A 1P CB (3 OFF) WITH NEW 40A 1P CB (3 OFF) FOR VODAFONE PSU ON THE DISTRIBUTION BOARD.
Information will be automatically generated to the IC Works Summary tab
| Page Completed |  |  |  |  | 13: Yes; 18: By Whom; 22: SARAVANAN S
| Company |  |  |  |  | 13: ALL TELECOS; 18: Date; 22: 2025-09-13

## TX
OM34440 Optus Site Feasibility Report | [5 empty] | V | 5 | Transmission Details Feasibility
Site No. |  | H8097 |  | Site Name |  |  | Austins Ferry
NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study.
| Are you performing a feasibility on the TX system? | [12 empty] | N/A
Details
Are you required to perform a feasibility study on the TX equipment?
Details
Existing Transmission Solution
| Suite Number |  | Operator |  | Vendor |  |  |  | Bearing |  | Height | In Use | Recovery Required |  | Variation
Details
Proposed Transmission Solution
| Suite Number |  | Operator |  | Vendor |  |  |  | Bearing |  | Height | In Use | Recovery Required |  | Variation
Details
Current JV Transmission Provider?
EJV Transmission Provider?
Is this an Optus EJV fibre site?
Details
Is there any equipment required to be recovered?
Details
Is there any unused or previously non recovered mW equipment that needs to be recovered either internally or on the tower?
Details
For EJV sites is Optus Fibre going to be provided?
Details
Is a leased line being used?
Leased line Manager contact details:
Details
Is there any equipment required to be recovered?
Details
| Existing MER TX Layout | [15 empty] | LIBRARY
| Suite | [8 empty] | Suite | [5 empty] | 44
[16 empty] | 43 | ELTEK APDP
| 44 | [8 empty] | 44 | [5 empty] | 42
| 43 | [8 empty] | 43 | [5 empty] | 41
| 42 | [8 empty] | 42 | [5 empty] | 40
| 41 | [8 empty] | 41 | [5 empty] | 39
| 40 | [8 empty] | 40 | [5 empty] | 38 | Ceragon IP10
| 39 | [8 empty] | 39 | [5 empty] | 37
| 38 | [8 empty] | 38 | [5 empty] | 36 | Aviat MSR
| 37 | [8 empty] | 37 | [5 empty] | 35
| 36 | [8 empty] | 36 | [5 empty] | 34
| 35 | [8 empty] | 35 | [5 empty] | 33 | Ceragon IP20
| 34 | [8 empty] | 34 | [5 empty] | 32
| 33 | [8 empty] | 33 | [5 empty] | 31
| 32 | [8 empty] | 32 | [5 empty] | 30 | 12 Way LGX Fibre TU
| 31 | [8 empty] | 31 | [5 empty] | 29
| 30 | [8 empty] | 30 | [5 empty] | 28 | Fibre Management
| 29 | [8 empty] | 29 | [5 empty] | 27
| 28 | [8 empty] | 28 | [5 empty] | 26 | Krone 1 - 15 Way
| 27 | [8 empty] | 27 | [5 empty] | 25
| 26 | [8 empty] | 26 | [5 empty] | 24
| 25 | [8 empty] | 25 | [5 empty] | 23
| 24 | [8 empty] | 24 | [5 empty] | 22 | Alcatel 1642
| 23 | [8 empty] | 23 | [5 empty] | 21
| 22 | [8 empty] | 22 | [5 empty] | 20
| 21 | [8 empty] | 21 | [5 empty] | 19
| 20 | [8 empty] | 20 | [5 empty] | 18
| 19 | [8 empty] | 19 | [5 empty] | 17
| 18 | [8 empty] | 18 | [5 empty] | 16
| 17 | [8 empty] | 17 | [5 empty] | 15
| 16 | [8 empty] | 16 | [5 empty] | 14
| 15 | [8 empty] | 15 | [5 empty] | 13
| 14 | [8 empty] | 14 | [5 empty] | 12
| 13 | [8 empty] | 13 | [5 empty] | 11
| 12 | [8 empty] | 12 | [5 empty] | 10
| 11 | [8 empty] | 11 | [5 empty] | 9
| 10 | [8 empty] | 10 | [5 empty] | 8
| 9 | [8 empty] | 9 | [5 empty] | 7
| 8 | [8 empty] | 8 | [5 empty] | 6
| 7 | [8 empty] | 7 | [5 empty] | 5
| 6 | [8 empty] | 6 | [5 empty] | 4
| 5 | [8 empty] | 5 | [5 empty] | 3
| 4 | [8 empty] | 4 | [5 empty] | 2
| 3 | [8 empty] | 3 | [5 empty] | 1
| 2 | [8 empty] | 2
| 1 | [8 empty] | 1
| Proposed MER TX Layout | [15 empty] | LIBRARY
| Suite | [8 empty] | Suite | [5 empty] | 44
[16 empty] | 43 | ELTEK APDP
| 44 | [8 empty] | 44 | [5 empty] | 42
| 43 | [8 empty] | 43 | [5 empty] | 41
| 42 | [8 empty] | 42 | [5 empty] | 40
| 41 | [8 empty] | 41 | [5 empty] | 39
| 40 | [8 empty] | 40 | [5 empty] | 38 | Ceragon IP10
| 39 | [8 empty] | 39 | [5 empty] | 37
| 38 | [8 empty] | 38 | [5 empty] | 36 | Aviat MSR
| 37 | [8 empty] | 37 | [5 empty] | 35
| 36 | [8 empty] | 36 | [5 empty] | 34
| 35 | [8 empty] | 35 | [5 empty] | 33 | Ceragon IP20
| 34 | [8 empty] | 34 | [5 empty] | 32
| 33 | [8 empty] | 33 | [5 empty] | 31
| 32 | [8 empty] | 32 | [5 empty] | 30 | 12 Way LGX Fibre TU
| 31 | [8 empty] | 31 | [5 empty] | 29
| 30 | [8 empty] | 30 | [5 empty] | 28 | Fibre Management
| 29 | [8 empty] | 29 | [5 empty] | 27
| 28 | [8 empty] | 28 | [5 empty] | 26 | Krone 1 - 15 Way
| 27 | [8 empty] | 27 | [5 empty] | 25
| 26 | [8 empty] | 26 | [5 empty] | 24
| 25 | [8 empty] | 25 | [5 empty] | 23
| 24 | [8 empty] | 24 | [5 empty] | 22 | Alcatel 1642
| 23 | [8 empty] | 23 | [5 empty] | 21
| 22 | [8 empty] | 22 | [5 empty] | 20
| 21 | [8 empty] | 21 | [5 empty] | 19
| 20 | [8 empty] | 20 | [5 empty] | 18
| 19 | [8 empty] | 19 | [5 empty] | 17
| 18 | [8 empty] | 18 | [5 empty] | 16
| 17 | [8 empty] | 17 | [5 empty] | 15
| 16 | [8 empty] | 16 | [5 empty] | 14
| 15 | [8 empty] | 15 | [5 empty] | 13
| 14 | [8 empty] | 14 | [5 empty] | 12
| 13 | [8 empty] | 13 | [5 empty] | 11
| 12 | [8 empty] | 12 | [5 empty] | 10
| 11 | [8 empty] | 11 | [5 empty] | 9
| 10 | [8 empty] | 10 | [5 empty] | 8
| 9 | [8 empty] | 9 | [5 empty] | 7
| 8 | [8 empty] | 8 | [5 empty] | 6
| 7 | [8 empty] | 7 | [5 empty] | 5
| 6 | [8 empty] | 6 | [5 empty] | 4
| 5 | [8 empty] | 5 | [5 empty] | 3
| 4 | [8 empty] | 4 | [5 empty] | 2
| 3 | [8 empty] | 3 | [5 empty] | 1
| 2 | [8 empty] | 2
| 1 | [8 empty] | 1
Fill in the Scope of Works Summary box below with as much details as possible relating to the proposed transmission upgrade site works.
Information will be automatically generated to the IC Works Summary tab
| Page Completed |  |  |  | N/A |  |  |  |  | By Whom
| Company | [8 empty] | Date

## Floor Layout
OM34440 Optus Site Feasibility Report | [5 empty] | V | 5 | Floor Layout
Site No. |  | H8097 |  | Site Name |  |  | Austins Ferry
NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study.
| Are you performing a feasibility on the Floor Layout? | [9 empty] | Yes
Details
| Are you required to perform a feasibility study on the shelter floor layout ? | [10 empty] | Yes
Details
| Which side of the shelter are the feeders entering from? (Looking from door entry to rear wall) | [10 empty] | Other
| Details |  | Rear wall
| Is any additional cable tray required? | [10 empty] | No
Details
| If Yes, there adequate space for installation? | [10 empty] | N/A
Details
| Is a second gland window required for feeders? | [10 empty] | No
Details
Existing Floor Layout
| Proposed Floor Layout | Final Floor Layout
Fill in the Scope of Works Summary box below with as much details as possible relating to your proposed floor layout site works.
OPTUS NOTES: 1. REMOVE EXISTING OPTUS HUAWEI BBU AND DCDU FROM THE RACK AT G001F04. 2. INSTALL NEW 1 x ERICSSON BBU6672 FOR L7/NL9/L18/NL21/L26/NR35 IN RACK AT G001F04. 3. INSTALL NEW DCDU (1 OFF) TO POWER UP ERICSSON BBUs IN RACK AT G001F04. 4. ALL EXTERNAL ALARMS (ENVIRONMENTAL ETC) TO BE MIGRATED FROM UMTS BBU TO LTE/5G BBU, AS PER OPTUS STANDARDS, INCLUDING OM36991 RAN EQUIPMENT I&C STANDARDS. 5. ALL 3G CONTROLLED RET'S TO BE MIGRATED TO 4G/5G AS REQUIRED, ACCORDING TO OPTUS STANDARDS, INCLUDING OM38040 MIMO PORT PLUMBING BTS RET CONTROL DEPLOYMENT. 6. REMOVE ANY ON-SITE CCU'S AND CONVERT CCU CONTROLLED MHA'S TO BTS CONTROLLED 7. EXISTING KRONE PANEL TO BE UPGRADED TO RJ45 PATCH PANEL. INSTALL 1 x 6610 FOR PSU ALARM AT G000.F02. iDCDP NOTES: 8. REUSE EXISTING OPTUS 22-WAY LENMIC iDCDP (1 OFF) IN RACK AT G001F05. AND SWAP CBs ON PSU AND iDCDP AS PER LATEST GUIDELINE. HYBRID CABLE NOTES: 9. REUSE EXISTING OPTUS H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND SHARED H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) DC POWER UPGRADE: 10. REMOVE EXISTING OPTUS HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F03. 11. INSTALL NEW OPTUS 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F03. 12. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F03. 13. REPLACE EXISTING 32A 1P CB (3 OFF) WITH NEW 40A 1P CB (3 OFF) FOR OPTUS PSU ON THE DISTRIBUTION BOARD. 14. OPTUS POWER TOOL V12.7 APPROVED. 15. DIVERSIFY Tx FEEDS OVER 2 PSUs. APDP FEED A ON OPTUS PSU-1-O. FEED B ON VODAFONE PSU-2-V. AC POWER UPGRADE: 16. EXISTING OPTUS 50A THREE PHASE POWER SUPPLY IS SUFFICIENT FOR THE PROPOSED UPGRADE. VODAFONE NOTES: 17. REMOVE EXISTING VODAFONE HUAWEI BBU AND DCDU FROM THE RACK AT G001F02. 18. INSTALL NEW NOKIA AIRSCALE/AMID CHASIS 1 OFF WITH SUITABLE BB CARDS AS PER EBP IN RACK AT G001F02. 19. NOKIA AIRSCALE SHALL BE POWER UP VIA VODAFONE PSU IN RACK AT G000F04. 20. NOKIA TX ROUTER TO BE RELOACTED FROM RU7 TO RU18 OR HIGHER POSTION AT G000F02. iDCDP NOTES: 21. REUSE EXISTING VODAFONE 22-WAY LENMIC iDCDP (1 OFF) IN RACK AT G001F05. AND SWAP CBs ON PSU AND iDCDP AS PER LATEST GUIDELINE. HYBRID CABLE NOTES: 22. REUSE EXISTING VODAFONE H&S 9/18 HYBRID CABLE (1 OFF) (LENGTH: 40m) AND INSTALL NEW H&S 9/18 (10mm2) HYBRID CABLES (1 OFF) (LENGTH: 40m) DC POWER UPGRADE: 23. REMOVE EXISTING VODAFONE HUAWEI PSU (1 OFF) WITH EXISTING 3kW RECTIFIERS (6 OFF) AND LPFG12-100S BATTERY STRINGS (5 OFF) FROM THE RACK AT G000F04. 24. INSTALL NEW VODAFONE 27kW VERTIV PSU WITH NEW 3kW RECTIFIERS (6 OFF) AT G000F04. 25. INSTALL NEW LFeLi-48100ZN BATTERIES (5 OFF) IN RACK AT G000F04. 26. REPLACE EXISTING 32A 1P CB (3 OFF) WITH NEW 40A 1P CB (3 OFF) FOR VODAFONE PSU ON THE DISTRIBUTION BOARD.
Information will be automatically generated to the IC Works Summary tab
| Page Completed |  |  |  | Yes |  |  |  | By Whom | SARAVANAN S
| Company |  |  |  | ALL TELECOS |  |  |  | Date | 2025-09-13

## Antenna System
OM34440 Optus Site Feasibility Report | [5 empty] | V | 5 | Antenna System
Site No. |  | H8097 |  | Site Name |  | Austins Ferry
NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study.
Have you completed antenna system site works?
Existing Antenna System
| Details |  | Existing shared 1x 12p large antenna
Sector 1
Antenna Number
| Antenna Model |  |  |  | Huawei ASI4517R1
| Antenna Details |  |  |  | 11-J
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
| Frequency |  |  |  | 850/900 | 700/900 | 1800/2100 | 1800/2100 | 18/21/26 | 18/21/26
| Carrier Using Ports |  |  |  | Voda | Optus | Voda | Voda | Optus | Optus
| Orientation (degrees) |  |  |  | 0
| Electrical Down Tilt (degrees) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2
| Mechanical Down Tilt |  |  |  | 0
| Mounting Height (m) - AGL |  |  |  | 23.1
| Coordinates (Easting, Northing) |  |  |  | 55 ¦ 520051 ¦ 5263789
| RET Enabled on Antenna |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes
Feeder Type and Size
Feeder Length (metres)
| Hybrid Cable (DC&Fibre) |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes
| Antenna Number |  |  |  | Antenna 3 | [7 empty] | Antenna 4
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mechanical Down Tilt
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET Enabled on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
Sector 2
Antenna Number
| Antenna Model |  |  |  | Huawei ASI4517R1
| Antenna Details |  |  |  | 21-J
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
| Frequency |  |  |  | 850/900 | 700/900 | 1800/2100 | 1800/2100 | 18/21/26 | 18/21/26
| Carrier Using Ports |  |  |  | Voda | Optus | Voda | Voda | Optus | Optus
| Orientation (degrees) |  |  |  | 200
| Electrical Down Tilt (degrees) |  |  |  | 2 | 5 | 2 | 2 | 4 | 4
| Mechanical Down Tilt |  |  |  | 0
| Mounting Height (m) - AGL |  |  |  | 23.1
| Coordinates (Easting, Northing) |  |  |  | 55 ¦ 520051 ¦ 5263789
| RET on Antenna |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes
Feeder Type and Size
Feeder Length (metres)
| Hybrid Cable (DC&Fibre) |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes
| Antenna Number |  |  |  | Antenna 3 | [7 empty] | Antenna 4
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mechanical Down Tilt
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET Enabled on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
Sector 3
Antenna Number
| Antenna Model |  |  |  | Huawei ASI4517R1
| Antenna Details |  |  |  | 31-J
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
| Frequency |  |  |  | 850/900 | 700/900 | 1800/2100 | 1800/2100 | 18/21/26 | 18/21/26
| Carrier Using Ports |  |  |  | Voda | Optus | Voda | Voda | Optus | Optus
| Orientation (degrees) |  |  |  | 340
| Electrical Down Tilt (degrees) |  |  |  | 2 | 3 | 2 | 2 | 3 | 3
| Mechanical Down Tilt |  |  |  | 0
| Mounting Height (m) - AGL |  |  |  | 23.1
| Coordinates (Easting, Northing) |  |  |  | 55 ¦ 520051 ¦ 5263789
| RET on Antenna |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes
Feeder Type and Size
Feeder Length (metres)
| Hybrid Cable (DC&Fibre) |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes
| Antenna Number |  |  |  | Antenna 3 | [7 empty] | Antenna 4
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mechanical Down Tilt
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET Enabled on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
Sector 4
| Antenna Number |  |  |  | Antenna 1 | [7 empty] | Antenna 2
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mechanical Down Tilt
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
| Antenna Number |  |  |  | Antenna 3 | [7 empty] | Antenna 4
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mechanical Down Tilt
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET Enabled on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
Existing RF Plumbing
Concept or Detailed plumbing drawing to be completed in Microsoft Visio and embeded here. RF Drawings are to follow Optus RF Drawing Template Standards
Proposed Antenna System
| Details |  | Swap antennas to shared 1x 16p large antenna +2x AAU
Sector 1
Antenna Number
| Antenna Model |  |  |  | Commscope RRVV2VV-6533D-R8 | [7 empty] | Ericsson AIR3268 B78Y | [5 empty] | Nokia AVQL
| Antenna Details |  |  |  | 11-J | [7 empty] | 12-O | [5 empty] | 13-V
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 | Port 13&14 | Port 15&16 | Port 1&2 | [5 empty] | Port 1&2
| Frequency |  |  |  | 700/850 | 700/900 | 18/21/26 | 18/21/26 | 1800/2100 | 1800/2100 | 1800/2100 | 1800/2100 | 3500 | [5 empty] | 3600
| Carrier Using Ports |  |  |  | Voda | Optus | Optus | Optus | Voda | Voda | Voda | Voda | Optus | [5 empty] | Voda
| Orientation (degrees) |  |  |  | 80 | [7 empty] | 80 | [5 empty] | 80
| Electrical Down Tilt (degrees) |  |  |  | 2 | 2 | 2 | 2 | 4 | 4 | 4 | 4 | 6 | [5 empty] | -2
| Mechanical Down Tilt |  |  |  | 0 | [7 empty] | 0 | [5 empty] | 0
| Mounting Height (m) - AGL |  |  |  | 23.1 | [7 empty] | 24.1 | [5 empty] | 23.1
| Coordinates (Easting, Northing) |  |  |  | 55 ¦ 520051 ¦ 5263789 | [7 empty] | 55 ¦ 520051 ¦ 5263789 | [5 empty] | 55 ¦ 520051 ¦ 5263789
| RET Enabled on Antenna |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | N/A | [5 empty] | N/A
Feeder Type and Size
Feeder Length (metres)
| Hybrid Cable (DC&Fibre) |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [5 empty] | Yes
| Antenna Number |  |  |  | Antenna 3 | [7 empty] | Antenna 4
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET Enabled on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
Sector 2
Antenna Number
| Antenna Model |  |  |  | Commscope RRVV2VV-6533D-R8 | [7 empty] | Ericsson AIR3268 B78Y | [5 empty] | Nokia AVQL
| Antenna Details |  |  |  | 21-J | [7 empty] | 22-O | [5 empty] | 23-V
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 | Port 13&14 | Port 15&16 | Port 1&2 | [5 empty] | Port 1&2
| Frequency |  |  |  | 700/850 | 700/900 | 18/21/26 | 18/21/26 | 1800/2100 | 1800/2100 | 1800/2100 | 1800/2100 | 3500 | [5 empty] | 3600
| Carrier Using Ports |  |  |  | Voda | Optus | Optus | Optus | Voda | Voda | Voda | Voda | Optus | [5 empty] | Voda
| Orientation (degrees) |  |  |  | 200 | [7 empty] | 200 | [5 empty] | 200
| Electrical Down Tilt (degrees) |  |  |  | 2 | 5 | 4 | 4 | 3 | 3 | 3 | 3 | 6 | [5 empty] | -3
| Mechanical Down Tilt |  |  |  | 0 | [7 empty] | 0 | [5 empty] | 0
| Mounting Height (m) - AGL |  |  |  | 23.1 | [7 empty] | 24.1 | [5 empty] | 23.1
| Coordinates (Easting, Northing) |  |  |  | 55 ¦ 520051 ¦ 5263789 | [7 empty] | 55 ¦ 520051 ¦ 5263789 | [5 empty] | 55 ¦ 520051 ¦ 5263789
| RET on Antenna |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | N/A | [5 empty] | N/A
Feeder Type and Size
Feeder Length (metres)
| Hybrid Cable (DC&Fibre) |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [5 empty] | Yes
| Antenna Number |  |  |  | Antenna 3 | [7 empty] | Antenna 4
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET Enabled on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
Sector 3
Antenna Number
| Antenna Model |  |  |  | Commscope RRVV2VV-6533D-R8 | [7 empty] | Ericsson AIR3268 B78Y | [5 empty] | Nokia AVQL
| Antenna Details |  |  |  | 31-J | [7 empty] | 32-O | [5 empty] | 33-V
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 | Port 13&14 | Port 15&16 | Port 1&2 | [5 empty] | Port 1&2
| Frequency |  |  |  | 700/850 | 700/900 | 18/21/26 | 18/21/26 | 1800/2100 | 1800/2100 | 1800/2100 | 1800/2100 | 3500 | [5 empty] | 3600
| Carrier Using Ports |  |  |  | Voda | Optus | Optus | Optus | Voda | Voda | Voda | Voda | Optus | [5 empty] | Voda
| Orientation (degrees) |  |  |  | 340 | [7 empty] | 340 | [5 empty] | 340
| Electrical Down Tilt (degrees) |  |  |  | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | [5 empty] | -3
| Mechanical Down Tilt |  |  |  | 0 | [7 empty] | 0 | [5 empty] | 0
| Mounting Height (m) - AGL |  |  |  | 23.1 | [7 empty] | 24.1 | [5 empty] | 23.1
| Coordinates (Easting, Northing) |  |  |  | 55 ¦ 520051 ¦ 5263789 | [7 empty] | 55 ¦ 520051 ¦ 5263789 | [5 empty] | 55 ¦ 520051 ¦ 5263789
| RET on Antenna |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | N/A | [5 empty] | N/A
Feeder Type and Size
Feeder Length (metres)
| Hybrid Cable (DC&Fibre) |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [5 empty] | Yes
| Antenna Number |  |  |  | Antenna 3 | [7 empty] | Antenna 4
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET Enabled on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
Sector 4
| Antenna Number |  |  |  | Antenna 1 | [7 empty] | Antenna 2
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
| Antenna Number |  |  |  | Antenna 3 | [7 empty] | Antenna 4
Antenna Model
Antenna Details
| Port Number |  |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12 |  |  | Port 1&2 | Port 3&4 | Port 5&6 | Port 7&8 | Port 9&10 | Port 11&12
Frequency
Carrier Using Ports
Orientation (degrees)
Electrical Down Tilt (degrees)
Mounting Height (m) - AGL
Coordinates (Easting, Northing)
RET Enabled on Antenna
Feeder Type and Size
Feeder Length (metres)
Hybrid Cable (DC&Fibre)
Proposed RF Plumbing
Concept or Detailed plumbing drawing to be completed in Microsoft Visio and embeded here. RF Drawings are to follow Optus RF Drawing Template Standards
Fill in the Scope of Works Summary box below with as much details as possible relating to your proposed antenna upgrade site works.
WA ID 658102 - Upgrdae 5G (eJV OH) - TU Swap L7/I7/L18/L21/L26 + New TU L9/N9/N21/N35 + TU decom U9 Optus Site Category: Metro-High ACMA Pre-check for NR35: S145 passed all sectors 25/09/2025 updated Sec 1 azimuth to 80° External Scope of Work: Antenna: Shared 1x large 16p antenna Commscope RRVV2VV-6533D-R8 for all sectors Optus: Install 2x RRU (1x RRU4480 (L7/NL9) + 1x RRU4466 (L18/NL21/L26) per sector and plan for 6 OFF RRU Install 1x 850 rejection filter E14V00P21 per sector Install 1x NR35 AAU AIR3268 B78Y per sector Replace existing GPS with 1x Ericsson GPS GNSS Reuse existing 1x 9/18 hybrid cable and existing shared 1x 9/18 hybrid cable to be allocated to Optus Vodafone: Install 4x RRU 1x AHPB (N7) + 1x AHCA (L850) + 2x AHEGG (18/21) per sector Install 1x LB combiner COM2g E14F06P81 per sector Install 1x NR36 AAU AVQL per sector Install 1x Nokia GPS AYGE Reuse existing 1x 9/18 hybrid cable and install new 1x 9/18 hybrid cable
Information will be automatically generated to the IC Works Summary tab
| Page Completed |  |  |  | Yes |  |  |  |  | By Whom | [5 empty] | Carolina Cansino
| Company |  |  |  | CPS Tech |  |  |  |  | Date | [5 empty] | 2025-09-15
Note on C147: Plumbing diagram to be drawn in Excel (using drawing objects) for ease of future revisions
Note on H174: required for FC drawings
Note on H189: required for FC drawings
Note on Q189: required for FC drawings
Note on H206: required for FC drawings
Note on H221: required for FC drawings
Note on Q221: required for FC drawings
Note on H238: required for FC drawings
Note on H253: required for FC drawings
Note on Q253: required for FC drawings
Note on H269: required for FC drawings
Note on Q269: required for FC drawings
Note on H284: required for FC drawings
Note on Q284: required for FC drawings
Note on C291: Plumbing diagram to be drawn in Excel (using drawing objects) for ease of future revisions

## Photos
OM34440 Optus Site Feasibility Report |  |  |  |  | V | 5 | Photos Existing
Site No. |  | H8097 | Site Name |  | Austins Ferry
NOTE: If you answer 'No' to the below question you are not required to complete any other information on this page, unless under instruction from Optus or performing a feasibility study.
| Are you performing a feasibility which requires photos to be taken? | [8 empty] | Yes
Details
Naming Convention to be used explicitly below. If more than 1 photo taken of an item then up the end number
External Photos
| Photo Name Required |  |  |  |  | Comments |  |  |  | Supplied
| SiteID_ShelterExt(N,E,S,W) |  |  |  |  | The pictures must show the shelter/ OOC from NESW directions including the compound |  |  |  | Yes
| SiteID_Tower |  |  |  |  | Tower including new Feeders, MHA’s from ground level from NESW |  |  |  | Yes
| SiteID_MastheadExt |  |  |  |  | Includes MHA, Antenna cluster from ground level zoomed x10 from NESW |  |  |  | Yes
| SiteID_ShelterGlandEntryExternal |  |  |  |  | Gantry containing feeders entering the shelter gland window, taken from most suitable location |  |  |  | Yes
| SiteID_EarthBarTowerBase |  |  |  |  | Earth bar connections base of tower |  |  |  | Yes
| SiteID_EarthBarTowerTop |  |  |  |  | Earth bar connections top of tower |  |  |  | No
| SiteID_EarthBarShelter |  |  |  |  | Earth bar connections cable entry window outside of shelter |  |  |  | Yes
| SiteID_EarthExtMisc |  |  |  |  | Earth connections for any installed equipment on tower/pole |  |  |  | No
| SiteID_HardwareExt |  |  |  |  | Close ups of each installed piece of equipment (antennae, dish, MHA, diplexer etc |  |  |  | Yes
| SiteID_LabelsExt |  |  |  |  | Close ups of all labelling – in particular the base band cable label |  |  |  | Yes
Internal Photos
| Photo Name Required |  |  |  |  | Comments |  |  |  | Supplied
| SiteID_FloorLayout |  |  |  |  | Floor Layout Taken from Entry door or open area showing as much of the internal hardware inside the shelter as possible including the new BTS using a wide angle lens |  |  |  | Yes
| SiteID_BTSOverview |  |  |  |  | Shows clusters of BTS as installed |  |  |  | Yes
| SiteID_BTS_(Carrier,Freq) |  |  |  |  | Shows detailed overview picture of BTS |  |  |  | Yes
| SiteID_BTS_(Carrier,Freq) |  |  |  |  | Shows detailed overview picture of BTS |  |  |  | Yes
| SiteID_BTS_(Carrier,Freq) |  |  |  |  | Shows detailed overview picture of BTS |  |  |  | Yes
| SiteID_BTS_(Carrier,Freq) |  |  |  |  | Shows detailed overview picture of BTS |  |  |  | Yes
| SiteID_MER |  |  |  |  | Entire Miscellaneous Equipment Rack must be clear enough to see new Transmission radio card or mux where added |  |  |  | Yes
| SiteID_SkinnyMER |  |  |  |  | Entire Miscellaneous Equipment Rack must be clear enough to see new Transmission radio card or mux where added |  |  |  | Yes
| SiteID_Krone |  |  |  |  | Overview of entire Krone’s showing new E1’s alarms etc where added. Must be clear enough to read when zoomed |  |  |  | Yes
| SiteID_KroneRear |  |  |  |  | Shows rear of Krone cabling proving neat and functional for maintenance |  |  |  | No
| SiteID_RFTails |  |  |  |  | Entire tails from BTS to Feeder connection point |  |  |  | Yes
| SiteID_Combiners |  |  |  |  | Diplexers, Same Band Combiner’s Triplexer’s, DC Inserters etc |  |  |  | N/A
| SiteID_Earth |  |  |  |  | All earth connections |  |  |  | Yes
| SiteID_PowerSupply |  |  |  |  | Overview of Power Supply |  |  |  | Yes
| SiteID_EltekCB |  |  |  |  | Eltek Circuit Breakers |  |  |  | Yes
| SiteID_EltekCBLS |  |  |  |  | Eltek Circuit Breaker Legend Sheet or traffolyte on older DC systems |  |  |  | Yes
| SiteID_EltekVoltAmp |  |  |  |  | Eltek Smartpack LCD display showing current and voltage readings, All equipment must be operating at full capacity when taking this photo |  |  |  | Yes
| SiteID_GlandWindow |  |  |  |  | Gland Windows Penetrations |  |  |  | N/A
| Site ID_ RETACU |  |  |  |  | RET/MHA Control Unit |  |  |  | N/A
ACMA Photos (these need to be included in the Deployment Code Folder)
| Photo Name Required |  |  |  |  | Comments |  |  |  | Supplied
| SiteID_SiteEntranceLabel |  |  |  |  | RF warning label on Door/Hatch/Gate entrance etc restricting access to shelter or antennas. |  |  |  | Yes
| SiteID_NSASiteNumber |  |  |  |  | RFNSA NSA label showing number, take an overview photo if location not obvious |  |  |  | Yes
| SiteID_RF HazardSign |  |  |  |  | Should be located next to the Entrance label |  |  |  | Yes
| SiteID_AntennaLabels |  |  |  |  | Yellow Radiation warning label on back of antennas |  |  |  | Yes
| SiteID_AntennaAccessRestriction |  |  |  |  | Do Not Climb Label placed at the bottom of antenna poles |  |  |  | Yes
| SiteID_AntennaCluster(S1-6) |  |  |  |  | Taken in front of each antenna or cluster |  |  |  | Yes
| SiteID_ Overall SitePhoto |  |  |  |  | Ground level looking up at antennas from NESW |  |  |  | Yes
| SiteID_PhotoExtras | [8 empty] | Yes
• Please be mindful and take extra photos that may assist Optus as a reference. • Photos must have a resolution 1024x768 pixels or larger and be less than 400 kilobytes in size. • Name the folder SiteID_PhotoExtra • The date must be inserted into the bottom right corner of each photo. • Photos must be presented horizontally. FastStone Photo Resizer is a freeware program that is capable of these tasks. It is also available in a portable format. http://www.faststone.org/FSResizerDetail.htm Please refer to Derrimut M1300 eJV site folder or the pictures as attached, which are not extras but good samples.
| Page Completed |  |  | Yes |  |  |  | By Whom | SARAVANAN S
| Company |  |  | ALL TELECOS |  |  |  | Date | 2025-09-13

## Document Control
OM34440 Optus Site Feasibility Report |  | Document Control
V | 5
Version | Amendment |  | Section | Date | Author
1 | Document compilation. |  | All | 2011-03-23 | Stuart Leslie
2 | Complete overhaul converted to excel format, feasibility and Acceptance site folder. |  | All | 2011-05-12 | Stuart Leslie
2a | Antenna and SAE page updates. Added Scope of Works Summary page at end. |  | All | 2011-05-16 | Stuart Leslie
3 | Updated Plumbing template, added feasibility photo tab, included BOM and BOQ, Included summary tab |  | All | 2011-05-15 | Paul Tremlett NSN
3a | Combined Pauls changes above into version 2a |  | All | 2011-05-17 | Stuart Leslie
3b | Added MER tab and overall fixes |  | All | 2011-05-19 | Stuart Leslie
3c | Overall update and alignment |  | All | 2011-05-20 | Paul Tremlett NSN
3c-1 | Minor updates to format, DC power and BOM and cover sheet |  | All | 2011-05-25 | Paul Tremlett NSN
3d | Design tab, Attachments comment, Final Antennas System table amalgamated as Proposed/ Final, 3G Call testing updated for 3 Sectors, User Guide added. |  | All | 2011-07-13 | Stuart Leslie
3e | Total revision simplified complete structure and overall technicality |  | All | 2011-08-17 | Stuart Leslie
3f | updated BTS, Antennas System and RF plumbing tabs with more detail. |  | BTS, Ant Sys & RF | 2011-08-22 | Stuart Leslie
3g | Added Power Supply C/B requirements and DC feed lengths. Added Tail requirement and lengths to Details box in Antennas tab. |  | BTS, Ant Sys | 2011-09-01 | Stuart Leslie
3h | Changed SAED coordinates from AGD66 to GDA94. Documents acceptance 3G Commissioning docs. Corrected MW acceptance visibility, Antenna System tab-added Feeder Make. Site Access-Delivery questions added. Floor Layout questions |  | SAE tabs, Doc Accept, Ant Sys, Site Access ,Floor Layout | 2011-09-07 | Stuart Leslie
3i | Document overhaul, Power Calculator updated to support LTE, 3G Call testing updated to support 6 sectors. Added 4G Call testing tab. |  | All | 2012-05-08 | Stuart Leslie
3j | 3G Call testing modified to allow voice on carriers F2-F4 also. Total overhaul for Jve.2G Call testing Emergency numbers require sector only not per TRX. |  | All | 2012-05-30 | Stuart Leslie- Mark Sirotti
3k | 2G Call testing Emergency numbers require sector only not per TRX. Full upgrade for EJV requirement plus U900 LTE Projects. |  | All | 2012-08-02 | Stuart Leslie
3l | Entire Rebuild for EJV in alignment with Optus |  | All | 2012-08-22 | Stuart Leslie
3m | Added EME Review Form A & Form B. Removed Environmental Planning questions, Target Antenna Solution Tab & Site Visit Summary Report Removed, BTS tab access info moved over to Site Access Tab. |  | All | 2013-06-21 | Stuart Leslie
3n | replaced OHS tab with new WHS tab, added new BTSs into power calcs tab, updated antenna scenarios for Leyland project, general update for Leyland |  | Power Calcs, WHS, Antenna | 2014-01-29 | Clyde King
4 | Amalgamating new WHS form, previous OM and new updates re: Leyland, including: - fields for additional antennas and antenna coordinates - air can, efan & AC supply details updated - setting eJV-related fields to 'N/A' - field for nominating which BTS will control the RET - cleaning up drop-down lists - general tidy up and fixing up of cell references etc - replaced EME Forms A & B with updated forms |  | Various | 2014-02-10 | Clyde King
5 | Removed Form A and B Removed WHS tabs Reformated document Amended IC Works Summary Added Power Calculation Summary Report into DC Tab |  | All | 2015-10-12 | Sokchea Bin

## Data
OM34440 Optus Site Feasibility Report |  |  | DATA
V | 5
Yes/No | WHS ratings | Structure Type | Structure Type | Green | Mount | New | MER | Call | Shelter Material | Feeder location | Lead Site | Equipment Enclosure Type | Hardware Vendor | Cabinet | Technology | Band1 | Band | Operator | Transmission Type | DC Vendor | Quantity | Transmission Make | Landlord | Equipment Enclosure Type | Breaker allocation | Leadoperator | PlanningArea | RAG | PlanningCategory | CADeploymentCategory | Timeframes | RFCarrier | Yes/No/Pass/Fail | antenna model | Eeprom | MCF guidelines | TechBand
Yes | 1 | Monopole | Monopole |  |  | New |  |  | Sandwich Panel | Left | Optus | Sandwich Panel Shelter | NSN | DBS3800 | GSM | 700 | 700 | Optus | Carrier Ethernet | Eltek FP2 | 1 | Huawei CX600 | Optus | Shelter - standard 7.5m | O | Optus | Residential | Red | Maintenance | Existing Site (Sect 7) | 3 weeks | Optus | Yes | Commscope RV4PX310R | Standard site use - Version 81 (OPT-ECON81DC & OPT-ECON81AC) | Progress to "Del 2" | DE34 G900
No | 2 | Lattice Tower | Lattice Tower | Greenfield | Rack | Upgrade | MER | New | Brick | Right | Optus JVe | Brick Shelter | Huawei | BTS3900 | UMTS | 850 | 700/2600 | Voda | IP | Eltek FP1 | 2 | Alcatel 1662 Mux | Vodafone | Shelter - large | V | Vodafone | Commercial | Amber | I-SEPP 'exempt development' | New Site (Sect 6) | 10 weeks | Voda | No | Commscope R2V4PX310R | Hub site with Alcatel 1662 use - Version 82 (OPT-ECON82DC & OPT-ECON82AC) | Please complete "Form B" and escalate | Ultrasite G900
N/A | 3 | Street Furniture | Street Furniture | Existing | MER (Fill in MER Layout) | Recovery | Wall | Upgraded | Concrete | Other | VHA | Outdoor | Ericsson | BTS3900L | LTE | 900 | 700/21/26 | Telstra | Hybrid IP&E1 | Invensys | 3 | Alcatel 1642 Mux | Telstra | Shelter - small | TX |  | Industrial | Green | I-SEPP 'complying development' | Not applicable (DA site Sect 1.4.2) | 3 months | Other | Pass | Commscope RVVPX310R | Leave existing Eeprom |  | Flexi G900
| 4 | Rooftop | Rooftop |  | Wall Mount | Relocation | Other | N/A | Other | N/A | Voda JVe | In Built | N/A | BTS3900L-C | Other | 700/850 | 700/2100 | Other | E1 | Hawker | 4 | Aviat MSR | Crown Castle | Equipment room |  |  | Area of ES |  | Vic telecode 'exempt' |  | 6 months | Spare | Fail | Commscope RRV4-65D-R6-EC | N/A |  | DF34 G1800
| 5 | Street Light | Street Light |  | Floor | N/A | N/A |  | N/A |  | Telstra | Exchange | Other | Ultrasite | N/A | 700/900 | 850 | N/A | Satellite | Ext Cabinet | 5 | Fujitsu FLM150E | Other Master Site Agreement | Outdoor unit |  |  |  |  | DA / Planning Approval |  | 9 months | N/A | N/A | Prose 2G4WHF-01N |  |  | Ultrasite G1800
|  | N/A | N/A |  | Pole | None |  |  |  |  | Crown Castle | DAS |  | FCOA |  | 850/900 | 900 |  | Multidropped | Ericsson BBS | 6 | Nortel OM1400 (Hub) | Private Landlord | [10 empty] | Tongyu T2004L6R021 |  |  | Flexi G1800
| Work Phase | Other | Other |  | Other | [5 empty] | Other | IBC |  | ICS MER |  | 700/850/900 | 1800 |  | Other | Other | 7 | NSN Flexihopper MW | Other | [10 empty] | other (provide detail below) |  |  | Ultrasite U900
| Inspection |  |  |  | Other | [6 empty] | Street furniture |  | Eltek MER |  | 1800 | 2100 |  | N/A | N/A | 8 | FBX (Hubs for STM4) | N/A | [13 empty] | Flexi U900
| Build Phase |  |  |  | Other | [6 empty] | Equipment Room |  | Other |  | 2100 | 2300 |  |  |  | 9 | MNI MW | Road Authority | [13 empty] | Multi Radio U900
| Installation/Commissioning |  |  |  | Other | [6 empty] | Other |  | N/A |  | 2300 | 2600 |  |  |  | 10 | NSN DMR MW | Local Council | [13 empty] | Ultrasite U2100
| Maintenance |  |  |  | Other | [6 empty] | N/A |  |  |  | 2600 | 700/900 |  |  |  | 11 | Satellite Gear | [14 empty] | Flexi U2100
[5 empty] | Other | [10 empty] | 1800/2100 | 850/900 |  |  |  | 12 | Cisco Router | [14 empty] | DBS 3800 U900
| Heirarchy of Control |  |  |  | Other | [10 empty] | 1800/2300 | 1800/2300 |  |  |  | 13 | Ericsson 301 | [14 empty] | BTS3900 U900
| 1- Elimination |  |  |  | Other | [10 empty] | 2300/2600 | 18/21/23 |  |  |  | 14 | Ericsson 601 | [14 empty] | BTS3900L U900
| 2 - Isolation/Substitution |  |  |  | Other | [10 empty] | 18/21/23 | 1800/2600 |  |  |  | Other | Ceragon 1500HP | [14 empty] | DBS 3800 U2100
[16 empty] | 18/21/26 | 18/21/26 |  |  |  | N/A | Other | [14 empty] | BTS3900 U2100
[16 empty] | 18/23/26 | 18/21/23/26 |  |  |  |  | N/A | [14 empty] | BTS3900L U2100
[16 empty] | 21/23/26 | 2300/2600 | [19 empty] | BTS3900L G900
[16 empty] | 18/21/23/26 | 2100/2300 | [19 empty] | BTS3900L G1800
[16 empty] | Other | Other | [19 empty] | BTS3900
[16 empty] | N/A | N/A | [19 empty] | N/A
[16 empty] | 1800/2600 | [20 empty] | Other
2100/2300
2100/2600